**How to Check Eyewash Station:**

1. Hold the handle and pull out.
2. Count to 10 seconds.
3. Push back the handle to close.
4. Check if the water is clear or not. It should be clear.
5. Check the water flow from each nozzle. The flow should be six inches long and the flows should cross in the center of the eyewash nozzle mount near there apex. Both streams should be equal.
6. Repeat Steps 1-5 two more times.
7. If the water is clear and the flow is good, write PASS on the sheet.
8. If the water is not clear or/and the flow is not good, repeat Steps 1-5 three more times.
9. If the water is not clear or/and the flow is not good, write FAIL on the sheet, report to Supervisor.

**\*\*\*Note**: If this is the first time this station has been tested in a long time, the water might still be dirty after test checking it 6 times, repeat steps (1-5) three more times.

**How to Check Shower Station:**

1. Move the large bucket underneath the shower-head to catch the water.
2. Connect the metal bar holder and yellow tube cloth.
3. Connect the metal bar holder with metal extension.
4. **These steps (4-7) needs 2 people to do:** One person holds the yellow tube cloth inside the bucket and bring the top of the yellow tube to cover the shower-head and the end of the yellow tube inside the bucket. Another person, pull the shower handle and count to 7.
5. Push the shower handle back.
6. Check the water if clear or not.
7. Repeat Steps 4-6 two more times.
8. If the water is clear, write PASS on the sheet.
9. If the water is not clear, repeat Steps 4-6 three more times.
10. If the water is still not clear, write FAIL on the sheet, report to Supervisor.
11. **This step needs 2 people to do:** After done, dump water from big bucket outside, onto plants. **WARNING:** Be careful not to injure yourself when dumping the water. Always dump the water with 2 people and when it reaches half of the bucket, then continue with the rest of your test check.

**\*\*\*Note:** If this is the first time this station has been tested in a long time, the water might still be dirty after test checking it 6 times, repeat steps (4-6) three more times.